## Site tool
Site performance: SGT-400 13 MW (public datasheet)
Blue cells are inputs. Results use correction curves from the calibrated gtperf model; see the Check sheet for their error against the full model.
Case
Case name |  | ISO | Temperate, sea level | Hot desert | Tropical coast | Cold, elevated
Site conditions
Ambient temperature | °C | 15 | 10 | 45 | 32 | -10
Site altitude | m | 0 | 30 | 300 | 10 | 1500
Relative humidity | % | 60 | 80 | 20 | 85 | 60
Inlet pressure loss | mbar | 0 | 8 | 10 | 8 | 8
Exhaust pressure loss | mbar | 0 | 15 | 25 | 20 | 15
Degradation, output | % | 0 | 0 | 0 | 0 | 2
Degradation, heat rate | % | 0 | 0 | 0 | 0 | 1
Derived
Ambient pressure (ISA) | mbar
Pressure ratio to ISO, delta | -
Correction factors (site = ISO x product)
Temperature, output | -
Altitude, output | -
Humidity, output | -
Inlet loss, output | -
Exhaust loss, output | -
Temperature, heat rate | -
Altitude, heat rate | -
Humidity, heat rate | -
Inlet loss, heat rate | -
Exhaust loss, heat rate | -
Temperature, exhaust flow | -
Altitude, exhaust flow | -
Humidity, exhaust flow | -
Inlet loss, exhaust flow | -
Exhaust loss, exhaust flow | -
Degradation factor, output | -
Degradation factor, heat rate | -
Site performance
Electrical output | MW
Heat rate (LHV) | kJ/kWh
Thermal efficiency (LHV) | %
Fuel heat input (LHV) | MW
Exhaust flow | kg/s
Exhaust temperature | °C
Fuel composition changes and part load need the full model (gtperf site, or the RunFullModel macro in gtperf.bas).

## Tables
temperature_C | t_power | t_heat_rate | t_exhaust_flow | t_exhaust_temp | rh_power | rh_heat_rate | rh_exhaust_flow | rh_exhaust_temp | inlet_power | inlet_heat_rate | inlet_exhaust_flow | inlet_exhaust_temp | exhaust_power | exhaust_heat_rate | exhaust_exhaust_flow | exhaust_exhaust_temp | control
-20 | 1.3352 | 0.92527 | 1.2435 | -53.8161 | -0.0005691 | 0.00028378 | -0.00057179 | -0.095983 | -0.0013912 | 0.00047176 | -0.00098642 | 0.17603 | -0.00040205 | 0.00046811 | 5.0167e-07 | 0.17386 | gas generator speed
-15 | 1.3007 | 0.93273 | 1.2127 | -43.8191 | -0.00086424 | 0.00043802 | -0.00087218 | -0.14378 | -0.0013954 | 0.0004789 | -0.00098643 | 0.17924 | -0.00040626 | 0.00047524 | 5.0072e-07 | 0.17704 | gas generator speed
-10 | 1.2677 | 0.94029 | 1.1831 | -33.7874 | -0.0012896 | 0.00066406 | -0.0013069 | -0.21157 | -0.0013996 | 0.00048604 | -0.00098643 | 0.18247 | -0.0004104 | 0.00048235 | 4.9597e-07 | 0.18025 | gas generator speed
-5 | 1.2315 | 0.94847 | 1.1527 | -24.3413 | 0.0024727 | 0.00035526 | -8.5782e-05 | 0.41077 | -0.0015369 | 0.00051438 | -0.0010424 | 0.16402 | -0.00054835 | 0.00051145 | -5.5926e-05 | 0.1619 | temperature
0 | 1.1695 | 0.96021 | 1.1127 | -18.5121 | 0.0036591 | 0.00046517 | -9.8535e-05 | 0.57625 | -0.0015605 | 0.00053364 | -0.0010482 | 0.16752 | -0.00057193 | 0.00053081 | -6.1828e-05 | 0.16538 | temperature
5 | 1.1104 | 0.97266 | 1.0739 | -12.5231 | 0.0053366 | 0.00058892 | -0.00010285 | 0.79467 | -0.0015858 | 0.00055412 | -0.0010547 | 0.17119 | -0.00059721 | 0.0005514 | -6.8367e-05 | 0.16903 | temperature
10 | 1.0539 | 0.98591 | 1.0364 | -6.3581 | 0.0076766 | 0.00071703 | -9.0286e-05 | 1.078 | -0.0016129 | 0.00057589 | -0.0010618 | 0.17504 | -0.00062432 | 0.00057332 | -7.5607e-05 | 0.17286 | temperature
15 | 1 | 1 | 1 | -1.7053e-12 | 0.010899 | 0.00083187 | -4.8376e-05 | 1.4395 | -0.001642 | 0.00059906 | -0.0010698 | 0.17907 | -0.00065342 | 0.00059666 | -8.3618e-05 | 0.17687 | temperature
20 | 0.94876 | 1.015 | 0.96478 | 6.5687 | 0.015283 | 0.00090451 | 4.0324e-05 | 1.8933 | -0.0016732 | 0.00062369 | -0.0010785 | 0.18328 | -0.00068463 | 0.00062151 | -9.2468e-05 | 0.18107 | temperature
25 | 0.90015 | 1.031 | 0.93064 | 13.3657 | 0.021174 | 0.00089097 | 0.00019911 | 2.4543 | -0.0017066 | 0.00064985 | -0.0010882 | 0.18768 | -0.00071807 | 0.00064793 | -0.00010222 | 0.18545 | temperature
30 | 0.85417 | 1.0481 | 0.89756 | 20.4076 | 0.029 | 0.00072808 | 0.00045774 | 3.1377 | -0.0017423 | 0.00067756 | -0.0010987 | 0.19223 | -0.00075383 | 0.00067596 | -0.00011295 | 0.19 | temperature
35 | 0.81087 | 1.0662 | 0.8655 | 27.71 | 0.039277 | 0.00032916 | 0.00085308 | 3.9594 | -0.0017804 | 0.00070683 | -0.0011103 | 0.19693 | -0.00079199 | 0.0007056 | -0.0001247 | 0.19469 | temperature
40 | 0.7703 | 1.0855 | 0.83444 | 35.2863 | 0.05263 | -0.00042232 | 0.0014326 | 4.9356 | -0.001821 | 0.00073761 | -0.001123 | 0.20172 | -0.00083262 | 0.00073683 | -0.00013758 | 0.19948 | temperature
45 | 0.73252 | 1.106 | 0.80435 | 43.1487 | 0.069832 | -0.0016915 | 0.0022755 | 6.0812 | -0.0018642 | 0.00076991 | -0.001137 | 0.20656 | -0.00087605 | 0.00076968 | -0.00015183 | 0.20435 | temperature
50 | 0.69756 | 1.1277 | 0.77518 | 51.3127 | 0.092029 | -0.0037889 | 0.0036175 | 7.3904 | -0.0019115 | 0.00080414 | -0.0011532 | 0.21151 | -0.00092372 | 0.00080465 | -0.00016836 | 0.20934 | temperature
Ratios to ISO for t_*; exhaust temperature columns are kelvin. rh_* per unit RH about 60%, inlet_* per mbar of inlet loss, exhaust_* per mbar of exhaust loss, all at sea level.
power_MW | heat_rate | exhaust_flow | exhaust_temp_C
12.9 | 10294 | 40 | 550.1992

## Check
Workbook formulas against the full gtperf model
Full-model values were computed when the workbook was generated, for the cases as generated. If you change a case on the Site tool sheet the error column no longer applies.
Case | Quantity | Full model | Workbook | Error
ISO | Output, MW | 12.9
ISO | Heat rate, kJ/kWh | 10294
ISO | Exhaust flow, kg/s | 40
ISO | Exhaust temperature, °C | 550.1992
Temperate, sea level | Output, MW | 13.2647
Temperate, sea level | Heat rate, kJ/kWh | 10285.5505
Temperate, sea level | Exhaust flow, kg/s | 40.907
Temperate, sea level | Exhaust temperature, °C | 548.0783
Hot desert | Output, MW | 8.489
Hot desert | Heat rate, kJ/kWh | 11725.8628
Hot desert | Exhaust flow, kg/s | 30.5214
Hot desert | Exhaust temperature, °C | 598.6244
Tropical coast | Output, MW | 10.5487
Tropical coast | Heat rate, kJ/kWh | 11074.2175
Tropical coast | Exhaust flow, kg/s | 34.952
Tropical coast | Exhaust temperature, °C | 579.7551
Cold, elevated | Output, MW | 13.0946
Cold, elevated | Heat rate, kJ/kWh | 9908.1583
Cold, elevated | Exhaust flow, kg/s | 39.1117
Cold, elevated | Exhaust temperature, °C | 521.3994

## About
gtperf site performance tool
Engine: SGT-400 13 MW (public datasheet).
Method
The Tables sheet holds corrections computed from the calibrated gtperf off-design model at sea level, every 5 °C from -20 to 50 °C:
t_*: output, heat rate and exhaust flow as ratios to ISO, exhaust temperature as a change in K.
rh_*, inlet_*, exhaust_*: linear sensitivities to humidity and to inlet and exhaust pressure loss.
Altitude is applied as the ISA pressure ratio delta (output and flow scale with delta, heat rate and exhaust temperature do not), which is exact for dry air by similarity.
Losses are divided by delta because their effect depends on the loss as a fraction of ambient pressure.
Effects are applied in a fixed order and multiplied, matching gtperf.site.site_performance.
Limits
Base load, natural gas as calibrated, new and clean unless degradation is entered. Fuel changes, part load and transient behaviour need the full model.
Regenerating
gtperf excel examples/sgt400_13mw.toml gtperf_site_tool.xlsx
VBA module (optional)
excel/gtperf.bas adds worksheet functions (GT_INTERP, GT_ISA_PRESSURE, GT_SITE_POWER and others) and a RunFullModel macro that sends each case to the Python model and writes the results under the sheet. Import it with Alt+F11, File > Import File, then save as .xlsm.
All engine data are from public datasheets or synthetic. Not for commercial use.
Settings for RunFullModel
gtperf command
gtperf
Datasheet file
/home/claude/gtperf/examples/sgt400_13mw.toml